## Slide 1: Passage of year presentation Reconstruction and Analysis of the Energy Demand of a Healthcare Facility
Department: Industrial Engineering
Ph.D Cycle: XXXV
Candidate: Marco Zini
(DT30464)
Tutors: Ing. Alessandro Bianchini
Prof. Ing. Carlo Carcasci
Prof. Ing. Giampaolo Manfrida

## Slide 2: Introduction
The energy demand in healthcare facilities is at a large extent constant during the day and throughout the year
  Due to specific constraints
    Service continuity
    Indoor air quality
It is difficult to define reference characteristics for the energy demand
  It is strongly connected with the specific activities/services carried out within each structure
Aim of the study:
Reconstruct and analyse the energy demand of the Healthcare Facility
Provide a simplified representation of the healthcare facility energy demand
Develop a BEM model prototype in energy plus environment based on the preceding analyses

## Slide 3: Healthcare Facility Overview
Building characteristics
  Total Surface: 12'000 m2
  Historic Building
    Majority of the offices
  Extension Area
    Healthcare core activities
    Technical Systems
Thermal Power Plant
  Hot water generators (x4, Qtot= 2800 kWth)
  Steam generators (x3, Qtot = 600 kWth)
Water Cooling System
  Refrigerators (x3, Wel = 960 kWel)
  Evaporative Towers (x6)
Air Handling System
  27 Units for Building Extension
  2 Units for the Historic Building

## Slide 4: Monthly Consumption - Electric and Thermal Energy
Electric Energy consumptions
July  +50% of the February energy demand
Massive cooling and ventilation requirements
Thermal Energy consumptions
Heating
Domestic Hot Water

## Slide 5: Monthly averaged daily Power Loads - 2019 VS. 2020
Weekdays
Tmean (°C) | February | March | April | May | June | July | August
2019 | 9.68 | 11.66 | 14.02 | 15.63 | 25.35 | 27.21 | 26.88
2020 | 9.50 | 9.24 | 13.46 | 19.00 | 21.38 | 25.56 | 25.54

## Slide 6: Correlation Analysis

## Slide 7: Correlation Analysis - Healthcare Facility Parameters
Time
  Month of the year, (Month)
    Represented through a sinusoidal function with m = 1, … , 12
  Hour of the day, (Time)
    Represented through a sinusoidal function with t = 1, … , 24
  Day typology, (Day Typ)
  Time slot, (Timeslot)
Climate
  External Temperature, (T)
  Relative Humidity, (RH)
Healthcare activities
  Staff in Service, (Staff Srv)
  Core Activities, (core act)
    Global parameter composed by the number of exams performed during a specific time step

## Slide 8: Correlation Analysis - Pearson's correlation coefficients
W
Month
Time
Day
Typ
Time
slot
T
RH
Staff
Srv
Core
Act
W
1.00
Month
0.29
1.00
Time
-
0.21
0.00
1.00
Day
Typ
-
0.26
-
0.05
0.00
1.00
Timeslot
-
0.53
-
0.02
0.37
0.41
1.00
T
0.78
0.21
-
0.27
-
0.02
-
0.25
1.00
RH
-
0.14
-
0.12
0.14
0.06
0.14
-
0.17
1.00
Staff
Srv
0.32
-
0.22
-
0.17
-
0.71
-
0.55
0.12
-
0.13
1.00
Core
Act
0.15
0.00
0.00
0.26
0.07
0.28
-
0.01
-
0.12
1.00

## Slide 9: Correlation Analysis - Polynomial regression (Linear)
 | Tlim [°C] | ΔW [kW] | R2 T < Tlim | R2 T > Tlim
F1 | 19.80 | 29.05 | 0.20 | 0.37
F2 | 20.81 | 49.18 | 0.25 | 0.23
F3 | 18.10 | 64.38 | 0.18 | 0.21
Totale | 22.71 | 44.28 | 0.33 | 0.27

## Slide 10: Correlation Analysis - Polynomial regression (Quadratic)
 | Tlim [°C] | ΔW [kW] | R2 T < Tlim | R2 T > Tlim
F1 | 19.80 | 33.77 | 0.21 | 0.36
F2 | 20.81 | 46.55 | 0.29 | 0.24
F3 | 18.44 | 66.87 | 0.21 | 0.17
Totale | 22.71 | 40.27 | 0.36 | 0.27

## Slide 11: Monitoring System Electric Energy
The electrical cabinet is divided in:
Normal Section
  21 lines powered by electricity grid
Preferential section
  63 lines
  Can be powered by a generator installed within the structure

## Slide 12: Monitoring System - Data Analysis
Analyzed Period
  Start: February 12th 2020
  End: August 31th 2020
Electric Power Demand
  Total Power demand, Wtot
  Refrigerators, Refrig.
  Air Handling Units, AHU
  Pumps
  Departments, Dep.
  UPS
Time related parameters
  Month of the year, Month
  Hour of the day, Time
  TIme slot (F1-F2-F3)
Climate parameter
  External Temperature, T

## Slide 13: Monitoring System - Data Analysis
 | Wtot | Refrig. | AHU | Pumps | Dep. | UPS | Month | Time | Time slot | T
Wtot | - |  |  |  |  |  |  |  |  | 
Refrig. | 0.97 | - |  |  |  |  |  |  |  | 
AHU | 0.80 | 0.68 | - |  |  |  |  |  |  | 
Pumps | 0.82 | 0.82 | 0.63 | - |  |  |  |  |  | 
Dep. | 0.44 | 0.25 | 0.49 | 0.13 | - |  |  |  |  | 
UPS | 0.24 | 0.09 | 0.28 | -0.20 | 0.76 | - |  |  |  | 
Month | -0.79 | -0.86 | -0.46 | -0.88 | -0.01 | 0.23 | - |  |  | 
Time | -0.16 | -0.15 | -0.13 | -0.05 | -0.12 | -0.23 | 0.00 | - |  | 
Time slot | -0.43 | -0.26 | -0.49 | -0.09 | -0.82 | -0.78 | 0.00 | 0.33 | - | 
T | 0.83 | 0.83 | 0.64 | 0.80 | 0.22 | 0.03 | -0.77 | -0.38 | -0.26 | -
  with t = 1, … , 24
Time slot
  High correlation with
    Departments and UPS
  Intermediate correlation with
    global electric power demand
    Air Handling Units power demand
External Temperature (T)
  Strong correlation with Electric power demand and Month parameters
Month
  Represented through a sinusoidal function
    with m = 1, … , 12
  Strong correlation with Electric power demand related to Refrigeration and Air Handling
  Strong correlation with External Temperature
Time
  Weak correlation with all the selected parameters
  due to the behaviour of the daily power demand, which tents to remain constant within each time slot

## Slide 14: Monitoring System - Data Analysis
 | Wtot | Refrig. | AHU | Pumps | Dep. | UPS | Time slot | T
Wtot | - |  |  |  |  |  |  | 
Refrig. | 0.97 | - |  |  |  |  |  | 
AHU | 0.80 | 0.68 | - |  |  |  |  | 
Pumps | 0.82 | 0.82 | 0.63 | - |  |  |  | 
Dep. | 0.44 | 0.25 | 0.49 | 0.13 | - |  |  | 
UPS | 0.24 | 0.09 | 0.28 | -0.20 | 0.76 | - |  | 
Time slot | -0.43 | -0.26 | -0.49 | -0.09 | -0.82 | -0.78 | - | 
T | 0.83 | 0.83 | 0.64 | 0.80 | 0.22 | 0.03 | -0.26 | -
Departments and UPSs
  Strong dependency on time slot
    influenced by the healthcare activities
  weak influence on the total electric power demand
External Temperature resume also the Month influence on absorbed power
Time slot result to be a better choice in comparison to the Time parameter
Refrigeration and air conditioning systems (Refrig. , AHU, Pumps)
  strong influence on the electric energy demand behaviour (Wtot)
  strongly influenced by the External Temperature (T)
  scarce dependency on time slot parameter (Time slot)

## Slide 15: Building Energy Modelling
Preliminary model developed in Energy Plus

## Slide 16: Building Energy Modeling - Energy Plus
A preliminary model of the Healthcare Facility has been realized in the Energy Plus Environment

## Slide 17: Building Energy Modeling - Energy Plus
Chart: qth (MWh)
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Gas [kWh] | 688.0028 | 546.8103 | 476.4773 | 400.9629 | 350.6125 | 279.3281 | 279.162 | 283.017 | 296.6116 | 355.4225 | 462.0582 | 622.0912
Gas [kWh] VD | 722.4525 | 586.0235 | 563.4475 | 522.8835 | 359.0339 | 258.9232 | 193.8689 | 164.2881 | 261.6503 | 347.6978 | 470.0743 | 722.4525
Chart: wel (MWh)
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Model | 310.248 | 285.618 | 324.7598 | 328.1758 | 354.1403 | 534.1399 | 582.4148 | 546.8562 | 445.6424 | 377.4945 | 315.4199 | 308.8001
Real | 340.752 | 334.5918 | 392.5121 | 366.1276 | 366.1511 | 447.2137 | 500.1634 | 496.334 | 438.4614 | 435.06 | 378.7028 | 360.1638
Electric Energy
Thermal Energy

## Slide 18: Building Energy Modeling - Energy Plus
Typical winter weekday
Typical summer weekday

## Slide 19: Conclusions
It has been perform the analysis of the healthcare energy demand
  The main Energy Driver is the External Temperature
  Internal activity parameters seems to have lesser influence on electric energy demand
It has been provided a simplified representation of the healthcare energy requirements
More detailed study has been carried out on the monitoring system measures
  More than 50% of global yearly electric energy consumption is related to HVAC Systems
A preliminary model has been realized in Energy Plus environment
  Qualitative representation of the healthcare energy needs
Next Steps:
Improvement of the existing Energy Plus model
Application of AI algorithms on the available data
  development of a numerical tool in order to predict the healthcare electric energy demand

## Slide 20: Publications
Journal:
Balduzzi F., Zini M., Ferrara G., Bianchini A., 2019, "Development of a CFD methodology to reproduce the effects of macro turbulence on wind turbines and its applications to the particular case of a VAWT", Journal of Engineering for Gas Turbines and Power 141, 2019.
Balduzzi F., Zini M., Carbò Molina A., Bartoli G., De Troyer T., Runacres M. C., Ferrara G., Bianchini A., "Understanding the Aerodynamic Behavior and Energy Conversion of Small Darrieus Vertical Axis Wind Turbines in Turbulent Flows", Energies 2020, 13, 2936, 2020.
Conferences:
Bianchini A., Carcasci C., Manfrida G., Zini M., "Reconstruction and Analisys of the Energy Demand of a Healthcare Facility in Italy", 75° Congresso Nazionale ATI, 2020.
Future works:
Detailed analysis of the energy demand of a building through dedicated monitoring systems: The particular case of a healthcare facility in Italy
Application of AI algorithm to predict building energy demand
Building Energy Modelling of a healthcare facility in Italy
Numerical investigation on trigeneration system behaviour and related emissions

## Slide 21: Passage of year presentation Reconstruction and Analysis of the Energy Demand of a Healthcare Facility
Department: Industrial Engineering
Ph.D Cycle: XXXV
Candidate: Marco Zini (DT30464)
Tutors: Ing. Alessandro Bianchini
Prof. Ing. Carlo Carcasci
Prof. Ing. Giampaolo Manfrida

## Slide 22: Backup Slides Passage of year presentation
Department: Industrial Engineering
Ph.D Cycle: XXXV
Candidate: Marco Zini (DT30464)
Tutors: Ing. Alessandro Bianchini
Prof. Ing. Carlo Carcasci
Prof. Ing. Giampaolo Manfrida

## Slide 23: Monthly Consumption - Water

## Slide 24: Total Electric Power Measured data VS. Linear Function

## Slide 25: Total Electric Power Measured data VS. Quadratic Function

## Slide 26: Instantaneous Electric Power Demand - 2019 VS. 2020